# BACnet inputs

# Product Description

# zencontrol controller BACnet Inputs variant.

Provides an interface to query/modify information on connected DALI input.

## BACnet Standardized Device Profile (Annex L)

## BACnet Application Specific Controller (B-ASC)

BACnet Operator Workstation (B-OWS

BACnet Advanced Operator Workstation (B-AWS)

BACnet Operator Display (B-OD)

BACnet Building Controller (B-BC)

BACnet Advanced Application Controller (B-AAC)

BACnet Application Specific Controller (B-ASC)

BACnet Smart Sensor (B-SS)

BACnet Smart Actuator (B-SA)

BACnet Smart Actuator (B-SA)

## BACnet Interoperability Building Blocks supported (see Annex K in BACnet Addendum 135d):

## DS-RP-B Read Property

DS-RPM-B Read Property Multiple

DS-WP-B Write Property

DS-COV-B Change Of Value

NM-BBMDC-B BBMD Configuration

NM-FDR-A Foreign Device Registration

## Supported device binding methods:

## Receive Who-Is, send I-Am (BIBB DM-DDB-B)

Receive Who-Has, send I-Have (BIBB DM-DOB-B)

## Segmentation Capability:

## No ability to transmit segmented messages

## Data Link Layer Options

## BACnet IP, (Annex J)

BACnet IP, (Annex J), Foreign Device

ISO 8802-3, Ethernet (Clause 7)

ATA 878.1, 2.5 Mb. ARCNET (Clause 8)

ATA 878.1, EIA-485 ARCNET (Clause 8), baud rate(s):

MS/TP master (Clause 9), baud rate(s):

MS/TP slave (Clause 9), baud rate(s):

Point-To-Point, EIA 232 (Clause 10), baud rate(s):

Point-To-Point, modem, (Clause 10), baud rate(s):

LonTalk, (Clause 11), medium:

BACnet/ZigBee (ANNEX O)

Other:

## Networking options

## Router, Clause 6 - List all routing configurations(e.g. ARCNET-Ethernet, Ethernet-MS/TP, etc.): Annex H.3, BACnet Tunneling Router over UDP/IP

BACnet/IP Broadcast Management Device (BBMD)

BBMD supports registrations by Foreign Device

## Character Sets Supported

## ANSI X3.4

## Additional information

# Other protocols supported DALI, Modbus RTU, DMX

This controller supports a maximum of 128 simultaneous subscriptions.

## Standard object types supported:

# Unless otherwise stated:

All objects are not dynamically createable or deletable using BACnet CreateObject/DeleteObject

No range restrictions on properties exit.

## Device object type

Object identifier

Object Name

System Status

Vendor Name

Vendor Identifier

Model Name

Firmware Revision

Application Software Version

Description

Protocol Version

Protocol Revision

Protocol Services Supported

Protocol Object Types Supported

Max ADPU Length Accepted

Segmentation Supported (not supported)

ADPU Timeout

Number of ADPU Retries

Device Address Binding

Database Revision

## List of Supported Optional Properties:

## Description (writable)

Local_Time

Local_Date

UTC_Offset

Daylight_Saving_Status

Active COV Subscriptions

## List of Supported Propriety Properties:

| Property Identifier | Property Datatype | Meaning |
| --- | --- | --- |
| 512 | CharacterString | Fitting Number |

## Binary Value Object Type

### List Of Supported Required Properties:

Object Identifier

Object Name

Present Value

Status Flags

Event State

Out Of Service

## Instance Numbers and Notes:

## These Binary Value objects support COV subscriptions.

| Instance numbers | Description |
| --- | --- |
| 256:271 | Occupancy state of proprietary object 129 (DALI Occupancy Group) 0-15. |
| 272 | Indicates whether any DALI Gear or Devices are missing. |
| 273 | Indicates whether any DALI Gear are reporting a lamp failure |
| 274 | Indicates whether there is a DALI circuit failure |
| 275 | Indicates whether the controller is online and functioning normally |
| 288:303 | Lamp failure state of proprietary object 129 (DALI Occupancy Group) 0-15 |
| 304:319 | Gear failure state of proprietary object 129 (DALI Occupancy Group) 0-15 |
| 320:335 | Comms failure state of proprietary object 129 (DALI Occupancy Group) 0-15 |
| 336:399 | Lamp failure state of DALI Address 0-63 |
| 400:463 | Gear failure state of DALI Address 0-63 |
| 464:527 | Comms failure state of DALI Address 0-63 |
| 1000:1063 | Comms failure state of DALI Control Device 0-63 |

## Binary Output Object Type

### List Of Supported Required Properties:

Object Identifier

Object Name

Present Value

Status Flags

Event State

Out Of Service

## Instance Numbers and Notes:

## All instances are writable, unless indicated by RO (read only)

| Instance numbers | Description |
| --- | --- |
| 0:127 | LED indicators of DALI Momentary Switches present on the DALI bus |
| 256:383 | LED indicators of DALI Absolute Inputs present on the DALI bus |

To test behaviour of the Binary Output object and its COV, set the Out of Service state to true, and then manually set Present Value as desired

## Analog Input Object Type

### List Of Supported Required Properties:

Object Identifier

Object Name

Present Value

Status Flags

Event State

Out Of Service

## Instance Numbers and Notes:

## All instances are read only, unless indicated

| Instance numbers | Description |
| --- | --- |
| 0:63 | Lux levels reported by the Light sensor instances on the DALI bus (ordered by control device address) |

## Analog Value Object Type

### List Of Supported Required Properties:

Object Identifier

Object Name

Present Value

Status Flags

Event State

Out Of Service

## Instance Numbers and Notes:

## These Binary Value objects support COV subscriptions. All points are writable, unless specified RO (Read Only).

| Instance numbers | Description |
| --- | --- |
| 256:271 | DALI Light Level state of proprietary object 129 (DALI Occupancy Group) 0-15 |
| 272:287 | DALI Scene state of proprietary object 129 (DALI Occupancy Group) 0-15 |
| 288:303 | Inhibit state of proprietary object 129 (DALI Occupancy Group) 0-15. |
| 304:319 | Minimum Lux Level state of proprietary object 129 (DALI Occupancy Group) 0-15. RO |
| 320:335 | Maximum Lux Level state of proprietary object 129 (DALI Occupancy Group) 0-15. RO |
| 336:383 | System Variable state (0-47) of the controller (no pro/pre v2.1 pro) |
| 336:483 | System Variable state(0-147) of pro controllers after v2.1 |
| 1024 | a free running counter that will monotonically increase over time to represent the continued running of the control system |
| 1025 | current Profile of the Controller. Write a Profile number between 0 – 65534 to switch to that profile if it is currently present on the controller. If it is not, no action will be taken. If a profile is switched to with a non-low priority, write a value of -1 to return the controller to its regularly scheduled profile. |
| 1100:1115 | Dali Group Colour Temperatures in Mirek format. Pro controllers only |
| 1116:1179 | Dali Address 0-63 Arc Levels. Pro controllers only. |
| 1180:1243 | Dali Address 0-63 Colour Temperatures in Mirek format. Pro controllers only |
| 2048:4095 | The state of any dali 306 multisensors connected to the system. Each dali address has 32 possible instances, therefore, control device address 0, instance 0 is instance number 2048, control device address 1, instance 0 is 2079 etc etc. For more information, see the zencontrol knowledgebase on 306 multisensors |
| 4096:6687 | The state of a system variable that has been given an associated target and index. Each target can have up to 32 System variables associated with it. See “System Variables In BACnet” guide on zencontrol website for further information. To test behaviour of the Analog Value object and its COV, set the Out of Service state to true, and then manually set Present Value as desire |

## MultiState Input Object Type

### List Of Supported Required Properties:

Object Identifier

Object Name

Present Value

Status Flags

Event State

Out Of Service

## Instance Numbers and Notes:

## These Multistate Input objects support COV subscriptions.

| Instance numbers | Description |
| --- | --- |
| 0:127 | DALI Momentary Switches present on the DALI bus. |
| 128:255 | DALI PIR Sensors present on the DALI bus. |
| 256:383 | DALI Absolute Inputs present on the DALI bus |

## Momentary Switch states:

| State | Description |
| --- | --- |
| 1 | No Input – The Input Switch has not been pressed |
| 2 | Short Press A – Input Switch has been short pressed and is latched in state A |
| 3 | Short Press B – Input Switch has been short pressed and is latched in state B |
| 4 | Long Press A – Input Switch has been long pressed and is latched in state A |
| 5 | Long Press B – Input Switch has been long pressed and is latched in state B |
| 6 | Stuck – The Input Switch has been pressed for a long period of time and is reporting it is stuck |

Present Value When short pressing, the Present Value will toggle between Short Press A/B.

When long pressing, the Present Value will toggle between Long Press A/B.

## PIR Sensor States:

| State | Description |
| --- | --- |
| 1 | Unoccupied – Sensor has not detected motion in the last 30 seconds |
| 2 | Occupied – Sensor has detected motion in the last 30 seconds |

## Absolute input states:

| State | Description |
| --- | --- |
| 1 | Absolute Input is in an unknown state and will be queried |
| 2 | State 1 – Absolute Input is at 0 |
| 3 | State 2 – Absolute Input is at 1 |

## CharacterString Value Object Type

### List Of Supported Required Properties:

Object Identifier

Object Name

Object type

Present Value

Status Flags

## Instance Numbers and Notes:

| Instance numbers | Description |
| --- | --- |
| 320:383 | Fitting Number of DALI Address 0-63 |
| 384:447 | GTIN of DALI Address 0-63 |
| 448:511 | Serial Number of DALI Address 0-63 |
| 512:575 | OEM GTIN of DALI Address 0-63 |
| 576:639 | OEM Serial Number of DALI Address 0-63 |

## DALI Occupancy Group Object Type (Identifier 129)

### List Of Supported Required Properties:

Object Identifier

Object Name

Object type

## List Of Supported Proprietary Properties:

| Property Identifier | Property Datatype | Meaning | Validity |
| --- | --- | --- | --- |
| 513 | Boolean | Occupancy State | 0 = Unoccupied, 1 = Occupied |
| 514 | Unsigned | DALI Light Level (Arc Level) | 0-254 Arc Level, 255 if mixed |
| 515 | Unsigned | Current Scene (Writable) | 0-12, 255 no current scene |
| 516 | Unsigned | Sensor Inhibit Time (secs) | 0 = Disable Inhibit, 1-86400 Inhibit for secs |
| 517 | Signed | Min Lux Seen | -1 = no lux data, 0→ Reported Lux Data |
| 518 | Signed | Max Lux Seen | -1 = no lux data, 0→ Reported Lux Data |

## Instance Numbers and Notes:

| Instance number | Description |
| --- | --- |
| 0 | Dali Group 0 Object |
| .. | .. |
| 15 | Dali Group 15 Object |