## Bacnet Features
Bacnet | Extended Bacnet | Object Type | Identifier | R/W | Type | Target | Description | Data Type | Controller | Extended information
YES | YES | BV | 0:63 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Battery Fail State | Boolean | PRO Only
YES | YES | BV | 64:127 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Lamp Fail state | Boolean | PRO Only
YES | YES | BV | 128:191 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Comms Error | Boolean | PRO Only
YES | YES | BV | 192:255 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Lamp On state | Boolean | PRO Only
YES | YES | BV | 272 | R | Gear | Controller | Indicates whether any DALI Gear or Devices are missing. | Boolean
YES | YES | BV | 273 | R | Gear | Controller | Indicates whether any DALI Gear are reporting a lamp failure | Boolean
YES | YES | BV | 274 | R | Gear | Controller | Indicates whether there is a DALI circuit failure | Boolean
YES | YES | BV | 275 | R | Gear | Controller | Indicates whether the controller is online and functioning normally | Boolean
YES | YES | BV | 288:303 | R | Gear | Group | Lamp failure state of proprietary object 129 (DALI Occupancy Group) 0-15 | Boolean
YES | YES | BV | 304:319 | R | Gear | Group | Gear failure state of proprietary object 129 (DALI Occupancy Group) 0-15 | Boolean
YES | YES | BV | 320:335 | R | Gear | Group | Comms failure state of proprietary object 129 (DALI Occupancy Group) 0-15 | Boolean
YES | YES | BV | 336:399 | R | Gear | Address | Dali Address 0-63 Lamp failure state | Boolean
YES | YES | BV | 400:463 | R | Gear | Address | Dali Address 0-63 Gear failure state | Boolean
YES | YES | BV | 464:527 | R | Gear | Address | Dali Address 0-63 Comms failure state | Boolean
| YES | BV | 1000:1063 | R | Device | Address | Control Device Dali Address 0-63 Comms failure state | Boolean | PRO Only
| YES | BO | 0:127 | W | Device | Instance | Control Device - LED indicators of DALI Momentary Switches present on the DALI bus | Boolean | PRO Only
| YES | BO | 256:383 | W | Device | Instance | Control Device - LED indicators of DALI Absolute Inputs present on the DALI bus | Boolean | PRO Only
| YES | AI | 0:63 | R | Device | Instance | Control Device - Lux levels reported by the Light sensor instances on the DALI bus (ordered by control device address) | Boolean | PRO Only | All lux values are post calibration (if set)
YES | YES | AV | 0:63 | R | Gear | Emergency Address | Dali Address 0-63 Emergency DALI Address State | Unsigned | PRO Only | Obsolete indicator of address (ie, 0 = 0, 1 = 1)
YES | YES | AV | 64:127 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Rated Duration | Unsigned | PRO Only | Data is returned in 2 minute increments
YES | YES | AV | 128:191 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Failure Status | Unsigned | PRO Only | Bitwise: 0-CircuitFail,1-BatteryDurationFail,2-BatteryFail,3-EmergencyLampFailure,4-FunctionTestDelayExceeded,5-DurationTestDelayExceeded,6-FuncTestFailed,7-DurationTestFailed
YES | YES | AV | 192:255 | R | Gear | Emergency Address | Dali Address 0-63 Emergency Status | Unsigned | PRO Only | Bitwise: 0-InhibitMode,1-FuncTestDoneAndResultValid,2-DurationTestDoneAndResultValid,3-BatteryFullyCharged,4-FuncTestRequestPending,5-DurationTestRequestPending,6-IdentificationActive,7-PhysicallySelected
YES | YES | AV | 256:271 | R/W | Gear | Group | DALI Light Level state of proprietary object 129 (DALI Occupancy Group) 0-15 | Unsigned |  | 0-254, 255-Unknown
YES | YES | AV | 272:287 | R/W | Gear | Group | DALI Scene state of proprietary object 129 (DALI Occupancy Group) 0-15 | Unsigned |  | 0-15, 255-Unknown
YES | YES | AV | 288:303 | R/W | Gear | Group | Inhibit state of proprietary object 129 (DALI Occupancy Group) 0-15. | Unsigned |  | Time that a group has switch presses, occupancy sensor triggers disabled for
YES | YES | AV | 304:319 | R | Gear | Group | Minimum Lux Level state of proprietary object 129 (DALI Occupancy Group) 0-15. | Unsigned |  | Minimum lux currently measured by lux sensors targeting this group
YES | YES | AV | 320:335 | R | Gear | Group | Maximum Lux Level state of proprietary object 129 (DALI Occupancy Group) 0-15. | Unsigned |  | Maximum lux currently measured by lux sensors targeting this group
| YES | AV | 336:383 | R/W | System | Controller | System Variable state (0-47) | Unsigned |  | 32bit signed
| YES | AV | 336:483 | R/W | System | Controller | System Variable state(0-147) | Unsigned | PRO Only | 32bit signed
YES | YES | AV | 1024 | R/W | System | Controller | a free running counter that will monotonically increase over time to represent the continued running of the control system | Unsigned |  | Used for identifying that the system has reset
YES | YES | AV | 1025 | R/W | System | Controller | Current Profile of the Controller. Write a Profile number between 0 – 65534 to switch to that profile if it is currently present on the controller. If it is not, no action will be taken. If a profile is switched to with a non-low priority, write a value of -1 to return the controller to its regularly scheduled profile. | Unsigned
| YES | AV | 1110:1125 | R/W | Gear | Group | Dali Group Colour Temperatures in Mirek format. | Unsigned | PRO Only | Mirek = (1000000 / Kelvin)
| YES | AV | 1126:1189 | R/W | Gear | Address | Dali Address 0-63 Arc Levels. | Unsigned | PRO Only | 0-254, 255-Unknown
| YES | AV | 1190:1253 | R/W | Gear | Address | Dali Address 0-63 Colour Temperatures in Mirek format. | Unsigned | PRO Only | Mirek = (1000000 / Kelvin)
| YES | AV | 1254:1317 | R/W | Gear | Address | Dali Address 0-63 Emergency Function Test Control | Unsigned | PRO Only | Bold=Can be set. 0-Idle, 1-TestRequested,2-RequestSent,3-TestStopRequested, 4-Stopped, 5-TestScheduledOnDevice, 6-Running, 7-Passed, 8-Failed
| YES | AV | 1318:1381 | R/W | Gear | Address | Dali Address 0-63 Emergency Duration Test Control | Unsigned | PRO Only | Bold=Can be set. 0-Idle, 1-TestRequested,2-RequestSent,3-TestStopRequested, 4-Stopped, 5-TestScheduledOnDevice, 6-Running, 7-Passed, 8-Failed
| YES | AV | 1382:1445 | R/W | Gear | Address | Dali Address 0-63 Emergency Duration Test Result | Unsigned | PRO Only | Data is returned in 2 minute increments.
| YES | AV | 1382:1445 | R/W | Gear | Address | Dali Address 0-63 Emergency Emergency Mode | Unsigned | PRO Only | Bitwise: 0-RestModeActive,1-NormalModeActive, 2-EmergencyModeActive, 3-ExtendedEmergencyModeActive, 4-FuncTestInProgress, 5-DurationTestInProgress, 6-HardWiredInhibitActive,7-HardwiredSwitchOn
| YES | AV | 2048:4095 | R/W | Device | Address+Instance | The state of any dali 306 multisensors connected to the system. Each dali address has 32 possible instances, therefore, control device address 0, instance 0 is instance number 2048, control device address 1, instance 0 is 2079 etc etc. For more information, see the zencontrol knowledgebase on 306 multisensors | Unsigned | PRO Only
| YES | AV | 4096:6687 | R/W | System | Address+System Variable | The state of a system variable that has been given an associated target and index. Each target can have up to 32 System variables associated with it. See “System Variables In BACnet” guide on zencontrol website for further information. To test behaviour of the Analog Value object and its COV, set the Out of Service state to true, and then manually set Present Value as desire | Signed | PRO Only
| YES | MSI | 0:127 | W | Device | Address+Instance Number | DALI Momentary Switches present on the DALI bus. | Unsigned | PRO Only | Supports 2 instances , 0 &1
| YES | MSI | 128:255 | W | Device | Address+Instance Number | DALI PIR Sensors present on the DALI bus. | Unsigned | PRO Only | Supports 2 instances , 0 &1
| YES | MSI | 256:383 | W | Device | Address+Instance Number | DALI Absolute Inputs present on the DALI bus | Unsigned | PRO Only | Supports 2 instances , 0 &1
YES | YES | CS | 0:63 | R | Gear | Emergency Address | Fitting Number (Emergency Object) | String
YES | YES | CS | 64:127 | R | Gear | Emergency Address | GTIN (Emergency Object) | String
YES | YES | CS | 128:191 | R | Gear | Emergency Address | Serial Number (Emergency Object) | String
YES | YES | CS | 192:255 | R | Gear | Emergency Address | OEM GTIN (Emergency Object | String |  | Obsolete
YES | YES | CS | 256:319 | R | Gear | Emergency Address | OEM Serial number ( Emergency Object) | String |  | Obsolete
YES | YES | CS | 320:383 | R | Gear | Address | Fitting Number of DALI Address 0-63 | String
YES | YES | CS | 384:447 | R | Gear | Address | GTIN of DALI Address 0-63 | String
YES | YES | CS | 448:511 | R | Gear | Address | Serial Number of DALI Address 0-63 | String
YES | YES | CS | 512:575 | R | Gear | Address | OEM GTIN of DALI Address 0-63 | String |  | Obsolete
YES | YES | CS | 576:639 | R | Gear | Address | OEM Serial Number of DALI Address 0-63 | String |  | Obsolete
YES | YES | Proprietary 128 | 512 | R | Gear | Emergency Address | Fitting Number | String | PRO Only
YES | YES | Proprietary 128 | 514 | R | Gear | Emergency Address | DALI Address | Unsigned | PRO Only
YES | YES | Proprietary 128 | 515 | R | Gear | Emergency Address | Battry Failure Status | Boolean | PRO Only
YES | YES | Proprietary 128 | 516 | R | Gear | Emergency Address | Lamp Failure Status | Boolean | PRO Only
YES | YES | Proprietary 128 | 517 | R | Gear | Emergency Address | Lamp on Status | Boolean | PRO Only
YES | YES | Proprietary 128 | 518 | R | Gear | Emergency Address | Comms Error Status | Boolean | PRO Only
YES | YES | Proprietary 128 | 519 | R | Gear | Emergency Address | GTIN | String | PRO Only
YES | YES | Proprietary 128 | 520 | R | Gear | Emergency Address | Serial Number | String | PRO Only
YES | YES | Proprietary 128 | 521 | R | Gear | Emergency Address | OEM GTIN | String | PRO Only | Obsolete
YES | YES | Proprietary 128 | 522 | R | Gear | Emergency Address | OEM Serial Number | String | PRO Only | Obsolete
YES | YES | Proprietary 128 | 524 | R | Gear | Emergency Address | Rated Duration | Unsigned | PRO Only
YES | YES | Proprietary 128 | 525 | R | Gear | Emergency Address | DALI Failure Status | Unsigned | PRO Only
YES | YES | Proprietary 128 | 526 | R | Gear | Emergency Address | DALI Emergency Status | Unsigned | PRO Only
YES | YES | Proprietary 129 | 513 | R | System | Group | Occupancy State | Boolean |  | Controller has global setting for amount of time to consider a target unoccupied. If no occupancy sensors have reported within this time, group will be considered unoccupied
YES | YES | Proprietary 129 | 514 | R/W | System | Group | DALI Light Level (Arc Level) | Unsigned |  | 0-254, 255-Unknown
YES | YES | Proprietary 129 | 515 | R/W | System | Group | Current Scene (Writable) | Unsigned |  | 0-15, 255-Unknown
YES | YES | Proprietary 129 | 516 | R | System | Group | Sensor Inhibit Time (secs) | Unsigned |  | Time that a group has switch presses, occupancy sensor triggers disabled for
YES | YES | Proprietary 129 | 517 | R | System | Group | Min Lux Seen | Signed |  | Minimum lux currently measured by lux sensors targeting this group
YES | YES | Proprietary 129 | 518 | R | System | Group | Lux Maximum Value | Signed |  | Maximum lux currently measured by lux sensors targeting this group